## Sheet1
Item Number | Item Title | Item Description | Item Quantity | Unit of Measure | Consignee ID | Delivery Period (In number of days)
1 | Supplying of 1.5 TR Nominal Capacity invertor type Metal body | Supplying of 1.5 TR Nominal Capacity invertor type Metal body Ceiling or wall suspended Single circuit High Static pressure ductable split AC unit with EER not less than 9.5 BTU/W-h (not less than 2.8 w/w) having cooling capacity not less than 18000 BTU/Hr, Minimum 45 Pa static pressure suitable for operation on 230 V Single Phase 50 HZ AC supply having front flow type indoor unit, air cooled condenser, initial charge of eco friendly refrigerent gas as per ATC | 140 | Nos | eeechd | 30
2 | Installation, Testing and commissioning of of 1.5 TR Inverter type ductable Air cooled split AC unit as per item No.1 above in equipment Room | Installation, Testing and commissioning of of 1.5 TR Inverter type ductable Air cooled split AC unit as per item No.1 above in equipment Room as per ATC | 140 | Nos | eeechd | 30
3 | Providing and Fixing Heavt duty powder coated M S Stand of suitable size made out of suitable guage MS shee | Providing and Fixing Heavt duty powder coated M S Stand of suitable size made out of suitable guage MS shee as per ATC | 140 | Nos | eeechd | 30
4 | Supply and fixing of 3 core 2.5 sq mm control cum transmission wiring and AC power supply cable of shielded Copper conductor for looping between indoor and outdoor | Supply and fixing of 3 core 2.5 sq mm control cum transmission wiring and AC power supply cable of shielded Copper conductor for looping between indoor and outdoor as per ATC | 280 | Mtr | eeechd | 30
5 | Supply and fixing of 4 core 1.5 sq mm control cum transmission wiring and AC power supply cable of shielded Copper conductor for looping between indoor and outdoor | Supply and fixing of 4 core 1.5 sq mm control cum transmission wiring and AC power supply cable of shielded Copper conductor for looping between indoor and outdoor as per ATC | 280 | Mtr | eeechd | 30
6 | Supply Installation testing and commissioning including vaccumiazation and Nitrogen testing of | Supply Installation testing and commissioning including vaccumiazation and Nitrogen as per ATC | 700 | Mtr | eeechd | 30
7 | Supply Installation testing and commissioning including vaccumiazation and Nitrogen | Supply Installation testing and commissioning including vaccumiazation and Nitrogen as per ATC | 700 | Mtr | eeechd | 30
8 | Supplying and Fixing of 25 mm sizes of rigid UPVC piping from outlet socket of AC unit complete with elbow | Supplying and Fixing of 25 mm sizes of rigid UPVC piping from outlet socket of AC unit complete with elbow as per ATC | 700 | Mtr | eeechd | 30
9 | Supplying and fixing DP sheet steel enclosure on surface or recess along with 25 or 32 A 230 V C curve DP MCB | Supplying and fixing DP sheet steel enclosure on surface or recess along with 25 or 32 A 230 V C curve DP MCB as per ATC | 140 | Nos | eeechd | 30
10 | Supplying and fixing 5 amps to 32 amps rating, 240 or 415 volts C curve miniature circuit breaker suitable for inductive load of Single pole and neutral | Supplying and fixing 5 amps to 32 amps rating, 240 or 415 volts C curve miniature circuit breaker suitable for inductive load of Single pole and neutral as per ATC | 140 | Nos | eeechd | 30
11 | Providing and Fixing supply air grills of Powder coated Aluminum construction having a free area of not less than 70 percent without volume control dampers | Providing and Fixing supply air grills of Powder coated Aluminum construction having a free area of not less than 70 percent without volume control dampers as per ATC | 35 | Sqmtr | eeechd | 30
12 | Supplying and installing of 150 mm width 50 mm depth 1.6 mm thickness nominal size of perforated Hot Dipped Galvanised Iron cable tray | Supplying and installing of 150 mm width 50 mm depth 1.6 mm thickness nominal size of perforated Hot Dipped Galvanised Iron cable tray as per ATC | 50 | Mtr | eeechd | 30