## Sheet1
Item Number | Item Title | Item Description | Item Quantity | Unit of Measure | Consignee ID | Delivery Period (In number of days)
1 | PCC and STP poles 8.5, 11 and 13 Mtr | Carriage of following poles from Store centre or from any other place to the respective site of work through the Kachha Pacca road including the work of its loading & unloading at the respective ends, also including the work of dragging etc and also including the cost of labour, T and P carrier etc required for proper completion of work Dist 0 to 50 Kms | 270 | Nos | EDCALIGARH2CONSIGNEE | 21
2 | Carriage of line material | Carriage of line material viz LT Cable, Conductor, GI earth wire, Barbed wire, Cross Arm, Angle, Channel, Insulator, various Clamps, XLPE cable, Cable, Stone pad and other line material from Store centre or from any other place to the respective site of work through the Kachha Pacca road including the work of its loading and unloading at the respective end, also including the work of dragging etc and also including the cost of labour, T and P carrier etc required for proper completion of work Dist 0 to 50 Kms | 7000 | KG | EDCALIGARH2CONSIGNEE | 21
3 | PCC and STP poles 8.5, 11 and 13 Mtr | Erection of single support including complete H.T and L.T fittings with drilling and cutting as per RESSPO manual and as per direction of Engineer incharge including the cost of labour, T and P and carrier etc required for proper completion of work | 134 | Nos | EDCALIGARH2CONSIGNEE | 21
4 | PCC and STP poles 8.5, 11 and 13 Mtr | Erection of double and Section pole on following poles including including complete H.T and L.T fittings with drilling and cutting and the work of complete line as per RESSPO norms manual and as per direction of Engineer Incharge including the cost of labour, T and P and carrier etc required for proper completion of work | 64 | Nos | EDCALIGARH2CONSIGNEE | 21
5 | Installation and fixing of 11 KV TPMO. | Erection of double and Section pole on following poles including including complete H.T and L.T fittings with drilling & cutting and the work of complete line as per RESSPO norms manual and as per direction of Engineer Incharge including the cost of labour, T and P and carrier etc required for proper completion of work | 64 | Nos | EDCALIGARH2CONSIGNEE | 21
6 | Erection and Grouting of stay set | Erection and Grouting of stay set including the work of nozzling etc as per RESSPO manual and also including the cost of arrangement of all grouting material, labour, T and P etc required for proper completion of work | 140 | Nos | EDCALIGARH2CONSIGNEE | 21
7 | Providing and fixing | Providing and fixing of stay insulator | 140 | Nos | EDCALIGARH2CONSIGNEE | 21
8 | ACSR Weasal, Rabbit and Dog Conductor. | Laying, sagging, stringing, binding and jumpering etc of line conductor on the newly erected pole as per RESSPO manual and as per direction of supervising engineer, including the cost of arrangement of labour, T and P carrier etc required for proper completion of work | 20000 | Mtr | EDCALIGARH2CONSIGNEE | 21
9 | ABC Conductor | ABC Conductor 3x50+1x35+1x16 Sqmm and 3x95+1x70+1x16 Sqmm and 3x120+1x95+1x16 Sqmm and 1x16+1x25 Sqmm | 800 | Mtr | EDCALIGARH2CONSIGNEE | 21
10 | Grouting of PCC and STP poles | Grouting of PCC and STP poles 8.5, 11 and 13 Mtr Long as per RESSPO norms | 260 | Nos | EDCALIGARH2CONSIGNEE | 21
11 | plinth | Making the plinth of Steel poles | 12 | Nos | EDCALIGARH2CONSIGNEE | 21
12 | Fixing of earthing rod | Fixing of earthing rod as per RESSPO manual and as per direction of supervising engineer including the cost of labour, T and P etc Required for proper completion of work | 270 | Nos | EDCALIGARH2CONSIGNEE | 21
13 | Chopping of tree branches | Chopping of tree branches which are touching to HT and LT lines | 40 | Nos | EDCALIGARH2CONSIGNEE | 21
14 | Providing and Fixing of Clamps of LT | Providing and Fixing of Clamps of LT, Cross Arm Holding, F Clamp, Stay Clamp, Danger board clamp and all type clamps with Nut and Bolts as per actual site requirement | 320 | Nos | EDCALIGARH2CONSIGNEE | 21
15 | Providing and Fixing | Providing and Fixing of LT shackle insulator | 20 | Nos | EDCALIGARH2CONSIGNEE | 21
16 | Providing and Fixing | Providing and Fixing of missing Nut bolts and washer | 120 | KG | EDCALIGARH2CONSIGNEE | 21
17 | 25 KVA Transformer | Carriage and Installation from site to Store and store to site following capacity transformer including the work of its loading and unloading, dragging etc and also including the cost of labour and T and P etc required for proper completion earthing and Jumphering of work | 48 | Nos | EDCALIGARH2CONSIGNEE | 21
18 | 63 KVA Transformer | Carriage and Installation from site to Store and store to site following capacity transformer including the work of its loading and unloading, dragging etc and also including the cost of labour and T and P etc required for proper completion earthing and Jumphering of work | 12 | Nos | EDCALIGARH2CONSIGNEE | 21
19 | 100 KVA Transformer | Carriage and Installation from site to Store and store to site following capacity transformer including the work of its loading and unloading, dragging etc and also including the cost of labour and T and P etc required for proper completion earthing and Jumphering of work | 10 | Nos | EDCALIGARH2CONSIGNEE | 21
20 | 400 KVA Transformer | Carriage and Installation from site to Store and store to site following capacity transformer including the work of its loading and unloading, dragging etc and also including the cost of labour and T and P etc required for proper completion earthing and Jumphering of work | 4 | Nos | EDCALIGARH2CONSIGNEE | 21
21 | Dismentling of old PCC and STP poles | Dismentling of old PCC and STP poles for shifting after dismentling of all accessories. It includes the work of cartage, cost of labour, T and P carrier etc required for proper completion of work | 4 | Nos | EDCALIGARH2CONSIGNEE | 21
22 | Dismantling and removal | Dismantling and removal of existing conductor, cable, GI Wire from the various area preparing their coils and then stacking in the respective JEOs Store as per direction of Supervising Engineer It includes the work of cartage, cost of labour, T nad P carrier etc required for proper completion of work | 200 | Mtr | EDCALIGARH2CONSIGNEE | 21
23 | Erection of section | Erection of section Tee pole including fixing of all fittings as per RESPO norms | 8 | Nos | EDCALIGARH2CONSIGNEE | 21
24 | Carriage and Installation | Carriage and Installation of LT distribution box three phase distribution box from store centre Sarsol to pit site including loading and unloading at both ends mounting and fixing on pole also by making connections as per RESSPO norms | 32 | Nos | EDCALIGARH2CONSIGNEE | 21
25 | Provding and Fixing, Filling | Provding and Fixing and Filling of 3x70,3x120,3X185 11 KV XLPE heat shrinkable cable jointing kits indoor and outdoor type including the cost of labour T and P carrier etc for proper completion of work | 10 | Nos | EDCALIGARH2CONSIGNEE | 21
26 | Safe carriage | Safe carriage of 3x70,3x120,3X185,3x300 Sqmm 33 KV by 11 KV XLPE Cable from Store Center to respective site of work including loading and unloading at both ends for proper completion of work | 800 | Mtr | EDCALIGARH2CONSIGNEE | 21
27 | Laying of under ground cable | Laying of 3x70,3x120,3X185,3x300 Sqmm 33 KV and 11 KV under ground cable by straight through after digging trench of 600 mm wide, 1500 mm deep, providing the fine sand cushion beneath and above the cable The cable shall be duly protected by Ist class bricks, two on either side and third on top of the cable, laid in series one after the other. The work includes supplying of fine sand and bricks, filling and ramming of the left out soil, closing the trench and levelling Spare cable shall be left and buried in the trench in the shape of rings at both ends All material except cable, labour, T and P carrier etc, required for proper completion of work will be arranged by the contractor at his own cost | 800 | Mtr | EDCALIGARH2CONSIGNEE | 21
28 | Laying of Overhead cable | Laying of 3x70,3x120,3X185,3x300 Sqmm 33 KV and 11 KV Overhead cable work includes labour, T and P carrier etc, required for proper completion of work will be arranged by the contractor at his own cost | 100 | Mtr | EDCALIGARH2CONSIGNEE | 21
29 | Guarding of 11 KV Line by laying two nos | Guarding of 11 KV Line by laying two nos GI wire parallel and fixing of lacings tilli at a distance at 2 to 3 Mtr as per RESPO manual and also including the cost of arragement of labour, T and P etc required for proper completion of work | 700 | Mtr | EDCALIGARH2CONSIGNEE | 21
30 | Safe Carriage and Installation | Safe Carriage and Installation of 33KV by 11 KV CT and PT Pole Mounted metering unit on double pole after fixing of channel with M S Clamps and nuts bolts for holding the channel angle etc The unit body shall be earthed by connecting M S strip of size 1,8x1 finally connected to earthing rod of size 20mm x2540 mm 11 KV line shall be connected to unit as per instructions of SDO and AE M The M S Strip and earth rod shall be included in the scope of work | 4 | Nos | EDCALIGARH2CONSIGNEE | 21
31 | Safe carriage and Installation | Safe carriage and Installation of 33KV by 11 KV pilfer proof metering cubicle from store centre, Sarsol to site of work | 4 | Nos | EDCALIGARH2CONSIGNEE | 21
32 | Provding and Fixing Wearing | Provding and Fixing Wearing GI pipe 6 O dia on the feeder cable before mounting the cable on the double pole lifting, mounting and clamping of 11 KV feeder cable with boxes on the feeder double pole structure and making connections including supply | 4 | JOB | EDCALIGARH2CONSIGNEE | 21