## Technical Bid
प्रसारभारती / PRASAR BHARATI (भारतकालोकसेवाप्रसारक/ INDIA’S PUBLIC SERVICE BROADCASTER) अपरमहानिदेशककाकार्यालय(अभि.) (द.क्षे..) / O/o. ADDL. DIRECTOR GENERAL (E)(SZ) आकाशवाणीएवंदूरदर्शन / AKASHVANI& DOORDARSHAN स्वामीशिवानंदासालै, चेन्नई/ SWAMY SIVANANDA SALAI, CHENNAI – 600 005. e-mail:adgszpurchase@prasarbharati.gov.in
Technical bid
Tender : J-11014/3/2026-PURCHASE-ADG(E)-(SZ) Date: xx.07.2026
DSITC OF 11kV 3 PHASE, 630A, MOTORIZED SCADA COMPATIBLE, SF6 INSULATED OUTDOOR, 5Way RING MAIN UNIT (RMU)AND INTEGRATION WITH THE HT POWER SUPPLY SYTEM
1 | Name of bidder
2 | Quotation No & Date
3 | Complete Postal Address
4 | E-mail
5 | Phone/Cell
TECHNICAL SPECIFICATION FOR DSITC OF 11kV 3 PHASE, 630A, MOTORIZED SCADA COMPATIBLE, SF6 INSULATED OUTDOOR, 5Way RING MAIN UNIT (RMU)AND INTEGRATION WITH THE HT POWER SUPPLY SYTEM.
Sl.No | Description | Specification |  | Tenderer's offer / Compliance (Numerical value to be given)
1 | Scope
1 | The specification covers Design, pre dispatch testing, supply, installation, testing and commissioning of 11kV 3 phase, 630Amps, Motorized SCADA compatible (For monitoring and Controlling), SF6 Insulated Outdoor, 5Way Ring Main Unit (RMU) (LB – 2 Nos., CB- 3 Nos.) in accordance with the technical requirements mentioned in the specification and relevant standards, including civil foundation as per the recommendation of the manufacturer as required and as per TGSPDCL Hyderabad norms
RMU Design and CT/ PT ratio should be suitable for 320kVA Maximum demand
Integration of Pole Structure, 5 Way RMU, 4 Panel HT Switchgear Panels and 2 Nos of 500kVA Transformers by laying 3 core 120 Sqmm Aluminium incoming feeder cables from the pole structure or as decided by TGSPDCL, Hyderabad to 5way RMU and from RMU to indoor HT Switchgear Panels and from HT Switchgear Panels to the 500kVA two numbers indoor transformers through underground trench as per Electricity IS norms and Supply & Providing conventional type copper plate earthing for RMU (2 Nos) , as per drawings and finally testing the power supply system.
2 | STANDARDS
a | The equipment delivered shall be new and of high quality, suitable for the purpose it is intended for, free from defects and imperfections and of the classifications listed herein, or their equivalents, subject to acceptance by this office.
b | Materials used in the manufacture of the specified equipment shall be of the kind, composition and physical properties best suited to their various purposes and in accordance with the best engineering practices
c | The equipment design shall be suitable to render satisfactory operation under the conditions prevailing at site, and the equipment shall operate satisfactorily under normal load and voltage variations and frequency variations (50 c/s ± 3%) ensuring the safety, further include all necessary provisions ensuring the safety of the operating and maintenance personnel.
d | The applicable standards are as specified here below
2.1 | 11kV 3 phase Outdoor Ring Main unit
SECTION -I
2.2 | Key RMU Configurations of RING MAIN UNIT
RMU – left or right extensible with two incoming feeder lines and two outputs, Vacuum Circuit Breaker with short circuit withstand current 21 kA for 3 sec., manually spring charging mechanism
3 | Technical parameters
11 kV 3 phase RMU
3.1 | Scope of Work
Design, pre dispatch testing, supply, installation, testing and commissioning of new Ring Main Unit for connecting with two feeder cables to 4 Panel HT Switchgear and two 500kVA indoor transformers.
RMU shall be equipped with vacuum circuit breakers and a fault passage indicator (FPI).
Integration with the two feeder cable from the pole structure, laying of HT cables from feeder pole structure to RMU Panel and from RMU panel to HT Switchgear panel and from HT Switchgear Panels to 500kVA two numbers of indoor transformers and testing the power supply system
Work includes foundation for RMU, excavation of cable trench, laying of HT cable, filling of sand & bricks and closing of trench, providing cable markers etc.
Copper Plate earthing, resistance should be less than 1 ohm.50mmx3mm copper strip to be used for earth pits to equipment
Cable termination kits/lugs etc required for completing the installation including any civil works as per site condition
Sufficient space shall be provided in the LV compartment of RMU to accommodate feeder terminal unit.
The RMU shall be equipped with main-line load break switches and a fault passage indicator (FPI). Furthermore, to protect each of its lateral / transformer feeders, it shall be equipped with a corresponding set of circuit breakers and self-powered numerical relays. The RMU shall include potential-free contacts so as to connect to SCADA/DMS via FRTUs, so as to:
Monitor and control the open/closed status of the RMU circuit breakers and load break switches.
Monitor the local/remote position of RMU manually-operated switches that can be used to enable and disable remote monitoring.
Monitor the health of the power supply, which will include battery failure and low voltage indications
Monitor the open/closed status of RMU earthing switches.
Facility for remote reset of FPI
Monitor for low SF6 gas pressure indication.
Monitor for circuit breaker relay operations
Monitor for indication of main-circuit fault detected by the RMU’s FPI
3.1.1 | Environmental Conditions
All materials supplied shall be capable of operating under relevant environmental conditions listed as follows: · Maximum ambient air temperature : 45 ºC · Minimum ambient air temperature : 0 ºC · Average ambient air temperature : 45 ºC · Maximum relative humidity : 0-100 % · Average thunder storm days per annum : 10 · Average rainfall per annum : 400 mm · Maximum wind speed : 119 km/hr · Altitude above mean sea level : 1000 m
3.1.2 | Distribution Network Electrical Parameters
The main parameters of the distribution network are as follows: · Nominal system voltage : 11 kV (rms) · Highest system voltage : 12 kV (rms) · Number of phases : 3 · Frequency :50 Hz · Variation in frequency : 50 ±3% Hz · Type of earthing : Solid · Power frequency withstand voltage : 28 kV rms · Basic impulse withstand voltage : 75 kV peak
3.1.3 | Testing
The specified RMU shall be subject to type tests, routine tests, and acceptance tests. Where applicable, these tests shall be carried out as per the standards stated above.
3.1.4 | 11kV 3 phase, 630Amps, Motorized SCADA compatible ( Monitoring & Controlling), SF6 Insulated Outdoor, 5Way Ring Main Unit (RMU) TECHNICAL PARAMETERS
3.1.4.1 | The scope is supply of 11 kV 3 phase 5Way RMU suitable for Outdoor application.
3.1.4.2 | The RMU to be supplied shall be compact and shall meet the following requirements: • Easy to install • Safe and easy to operate • Compact • Low maintenance
3.1.4.3 | It shall include, within the same metal enclosure number of MV functional units required for connection, • Vacuum circuit breakers for two incoming feeders, 4 Panel HT Switchgear and two 500kVA indoor transformers. • Power supply including the battery bank for controlling the LBS and breakers • Load break switches, • Earthing Switches • Breakers • Relays • BUS PT metering module, FPI’s and other allied equipment • Dimensions of FRTU will be 1000 mm (H) X 600 mm (W) X 300 mm (D). Sufficient space shall be provided in the LV compartment of RMU to accommodate this FRTU. FRTU and MFT will be provided by TGSPDCL, Hyderabad
3.1.4.4 | Equipment and material conforming to any other standard, which ensures equal or better quality, may be accepted. In such case copies of English version of the standard adopted shall be submitted.
3.1.4.5 | The electrical installation shall meet the requirement of Indian Electricity Rules, 1956 as amended up to date, relevant IS code of practice and Indian Electricity Act, 1977. The Electricity Act, 2003 and Amendment if any shall also apply. In addition other rules and regulations applicable to the work shall be followed. In case any discrepancy the most stringent and restrictive one shall be binding.
3.1.4.6 | The high-tension switchgear offered shall in general comply with the latest issues including amendments of the Standards as per specification but not restricted to them.
3.1.4.7 | All design features of the proposed RMU, as described in the supplier’s bid and in the bid’s reference materials, shall be fully supported by the equipment actually delivered. The key design features include those that relate to: • Maintainability, expandability, and life span • Ability to operate in severe environmental conditions. • Immunity to electrical stress and disturbance. • Acceptable insulation properties. • Convenient interconnection features.
3.1.4.8 | MAKE OF RMU: ABB or SIEMENS or SCHNEIDER
3.1.5 | Battery
The DC batteries shall have sufficient capacity to supply power to the devices with a nominal backup of 8 hours: -To restore a depleted battery to 80% of full capacity in less than 8 hours. -To deliver the load of RMU’s trip coils, close coils, multifunction meters, and relays, spring charge motor.
The batteries shall be of sealed lead acid or Ni-Cad type, comply with IEC 60623 and shall have a minimum life of five (5) years at 25°C. Each battery cell (For Lead Acid Cell) shall come with a transparent housing for the ease of checking of the battery water level. The battery shall have the capability to close and open the switches for at least 10 close-open cycles (this must be verified by calculation). When sizing the AH capacity of the battery, the effect of aging shall be taken into consideration. The AH rating of the battery shall be greater than calculated AH but not less than 20AH
The battery charger shall be fully temperature compensated.
To prevent deep discharge of the batteries on loss of AC power source, the battery charger shall automatically disconnect all circuitry fed by the batteries following a user-adjustable time period or when the battery voltage falls below a preset value
The battery charger shall be provided with an alarm displayed at the local control panel and remotely at the SCADA (for monitoring) to account for any of the following conditions: - Low battery voltage - High battery voltage - Battery failed - Battery charger overvoltage - Grounded battery/battery-charger - Low electrolyte alarm - Input MCB off - Station AC supply fail - Battery Charger fail - Others according to manufacturer’s design
The capacity of battery and charger shall be declared in the Technical parameters.
3.1.5.1 | Battery Charger
The charger shall be designed to provide a well regulated DC supply to the load while float charging or quick charging the battery. The charger shall be the constant potential, current limiting fully automatic type. The charger shall automatically switch to float charge after the battery is restored to 80% of its nominal capacity under BOOST charge. The BOOST charge shall be automatically ON after an emergency discharge and the duration of BOOST charge shall be less than 8 hours.
The float charge voltage shall not vary by more than +/- 2% of the set value irrespective of AC input voltage variation of +/- 10 % and of load variation from 0% to 100%. The r.m.s ripple voltage across the battery shall not exceed 1% of the nominal output voltage.
The charger shall be protected against low battery voltage and short circuit at the output by employing current limiting feature. It shall also be protected against reversed battery voltage. Suitable protection shall be incorporated for DC output, transformer secondary, rectifier etc. The charger shall be designed to operate continuously at a temperature of 55°C. To ensure long service life for the charger, all semiconductor devices shall be of industrial grade. The following instrument and control shall be provided on the charger:-
• Mains ON/OFF input circuit breaker with Mains ON neon or LED indicator, DC output MCBs with spare. All MCBs shall be of double pole design with auxiliary voltage free contact. • BOOST selector switch, Voltmeter and Ammeter to measure charger/battery voltage and current. • All visual alarm indication shall be of LED type with its function clearly mentioned.
3.2 | Maintainability, Expandability, and Life Span
3.2.1 | Maintainability The Utility intends to be self-reliant for RMU maintenance. To this end, the Supplier shall provide the support, documentation, and training necessary to operate and repair the RMU. The Utility will prefers RMU designs that do not require periodic preventive maintenance and inspections. To facilitate expansion and maintenance, the RMUs should be of modular type.
3.2.2 | Expandability The whole switchgear (RMU) should be suitable for extension on at least one side either left or right.
3.2.3 | Life Span RMU shall have a design life of at least 20 years from the date of final acceptance. The Contractor shall make available, at no cost to the department, the manufacturing drawings, wiring diagrams, bill of material, foundation detail drawings, unpacking and transportation instructions, operation & maintenance manual, As-built drawings and other relevant documentation. The specific components of each component/sub-assembly shall be identified and referenced in Supplier-supplied documentation.
3.3 | RMU Features
3.3.1 | General
The 5 way RMUs shall be designed specifically for outdoor installation with ingress protection degree of IP54. They shall also be suitable for conditions in which they will be exposed to heavy industrial pollution, and high levels of airborne dust.
The outdoor RMU shall be conformably coated to meet the climatic conditions. In this respect, standards such as IEC 62271-200, covering equipment, systems, operating conditions, and environmental conditions shall apply. In particular, the RMU equipment shall have been type tested for IP54. Failure to conform to this requirement shall constitute grounds for rejection of the proposal
In addition to the above, materials promoting the growth of fungus or susceptibility to corrosion and heat degradation shall not be used, and steps shall be taken to provide rodent proof-ness.
3.3.2 | Corrosion Protection
The main SF6 tank, should be of 2.5 mm thick (minimum) stainless steel tank so as to have high corrosion resistance and ensure high longevity. The normal operating pressure shall be 1.2 bar @ 20 deg C. However offer with nominal operating gas pressure shall be as per manufacture standard and suitable to satisfy the rated dielectric strength. This tank containing SF6 should be hermetically welded and sealed for life, ensuring a leakage rate not more than 0.1 % per annum. Except for stainless steel, all steel surfaces that are not galvanized shall be treated to protect against corrosion. As a minimum, corrosion treatment shall include the following procedures:
The surface shall be cleaned to bare material by mechanical or chemical means
Must be powder coated by means of seven tank process
All outdoor metal enclosures shall be treated in 7 tank Pre-treatment process & should be painted with UV Resistant Pure Polyester Powder coating. The powder coated sheet steel fabrication shall fulfill 700 Hrs of Salt spray test. The thickness of Painting/Powder coating shall be of 80-90 microns to withstand tropical heat and extremes of weather.
3.3.3 | Immunity to Electrical Stress and Disturbance
The electrical and electronic components of the RMU shall conform to relevant standards concerning insulation, isolation, and the product shall comply with IEC 60270 Immunity to electrical stress & disturbance. The ability to meet these requirements shall be verified by type tests carried out by accredited test laboratories that are independent of the bidder and/or the manufacturer of the RMU components. Certified copies of all available type test certificates and test results shall be included as part of the bidder’s proposal.
3.3.4 | Minimum Insulation of Equipment
The RMUs shall be of SF6 gas-insulated type with normal operating pressure shall be 1.2 bar @ 20 deg C. However offer with nominal operating gas pressure shall be as per manufacture standard and suitable to satisfy the rated dielectric strength.
3.4 | Name plate Information
RMU nameplate information shall be determined in agreement with the Employer. This information may include for example • Name of manufacturer and country • Type, design, and serial number • Rated voltage and current • Rated frequency • Rated symmetrical breaking capacity • Rated making capacity • Rated short time current and its duration • Rated lightning impulse withstand voltage • Purchase Order number and date • Month and year of supply RMU shall also exhibit a Danger Board to indicate the presence of high voltage (11,000 V).
3.5 | Interconnecting Cables, Wiring, Connectors, and Terminal Blocks
The Contractor shall provide all interconnecting wires, cables, connectors, terminations and other wiring accessories such as terminal blocks required by the RMU
3.5.1 | Metallic Cables
All metallic cables and wiring shall be of required cross-section solid or multiple strands of round copper conductors and have flame retardant insulation. All wiring shall be neatly laced and clamped.
All wire and cable connectors and terminators shall be permanently labeled for identification. All connection points for external cables and wires shall be easily accessible for connection and disconnection and shall be permanently labeled. Conductors in multi-conductor cables shall be individually color-coded
3.5.2 | Connectors
• Nuts & Bolts type terminal blocks shall be provided in LV compartment for connectivity and to accommodate FRTU.. • 11kV RMU shall be provided with Vacuum circuit breakers(VCB). • VCB recommended make:ABB/Siemens/Schneider Electric
RMU FRTU CONNECTORS
• For ease of installation and maintenance, the interconnection between the RMU and the FRTU, (FRTU is not in the scope of the bidder) in a separate enclosure shall be supported by having heavy-duty terminal blocks with Nuts & Bolts type terminals shall be provided by the supplier for necessary cable terminations. In using a terminal block, no more than two cables or wires shall be connected to any of its individual terminals
• Making strips shall be used to identify all external connection blocks. Marking tags shall be read horizontally. All terminals to which battery or other high voltages are connected shall be provided with fireproof covers
• All individual status input, AC voltage input, and control output points shall be isolatable without the need to remove wiring by means of individual terminal blocks of the removable link type. In order to avoid open circuits on the secondary side of CTs, termination blocks with by-pass bridges shall be provided for all AC current inputs.
• Terminal blocks shall comply with IEC 60947-7-1 (2009): Low-voltage Switchgear and Control Gear, Part 7-1: Ancillary Equipment, Terminal Blocks for Copper Conductors.
3.5.3 | RMU Characteristics
• As a minimum, the RMUs shall be equipped with on-load break switches and a fault passage indicator (FPI), circuit breakers, and self powered numerical relays for the protection of transformer feeders, and provision for wiring for multifunction transducer (MFT is not in the scope of the bidder) for monitoring voltage, current, power, energy, and power factor readings and tripping and protection functionalities from the Communicable Numerical relay to be provided on the RMU. Each LBS shall be provided with 1No. FPI thus RMU shall be with 2 No. FPI. The Load Break Switches and earthing switches shall be housed in SF6 and the Circuit Breakers used in the RMU shall be vacuum interrupter type.
• In addition, each RMU shall be equipped with all necessary connectors, terminal blocks, and other accessories that will allow it to be connected to the FRTU, which in-turn will send required indications and measurements to the DMS via the communications system
3.5.4 | General Requirements
• The RMU shall include its own power supply, including battery and battery charger. In addition, RMU should have a bus connected PT panel (air insulated), which shall serve as the power supply’s 230 V AC input
• Within this context, the general requirements of the RMU shall include, but shall not be limited to provision of the following monitoring and control features:
• Positions of local/remote switches as used to control local and remote access to circuit breakers and load break switches
• Power supply indications including battery failure and voltage alarms
• Open/closed position of load break switches, circuit breakers, and earthing switches
• SF6 gas-pressure low indication
• Circuit breaker relay indications
• Indications of fault in the RMU’s main feeder circuit as detected by the FPI
• Load break switch and circuit breaker open/close control
• FPI reset control
3.6 | General Requirements
• Power supply indications • Mechanical Status indication for Open/closed position of break switch and earthing switches. • SF6 gas-pressure low indication. • Indications of fault in the RMU’s as detected by the FPI • Vacuum circuit breaker open/close control
3.7 | Parameter Requirements
The RMUs shall be suitable for cable networks of 630 Amps copper bus bar and loop cable networks of 400 Amps. The minimum design parameters to which their major components shall conform or exceed are summarized in the following tables
3.8 | BUSBARS:
The Busbars made up of copper of rating 630A shall be provided. All joints and connectors shall be SF6 insulated in accordance to this specification. Any component directly connected to the power cables shall also be capable of withstanding the DC test voltage applied to the cables.
Table 1: System Parameters
Table 2: Load Break Switch Parameters
Table 3: Vacuum Circuit Breaker Parameters
The 5 Way RMU switchgear shall be capable of withstanding the specified currents without damage in accordance with the latest versions of IEC 60694 (Common Specifications for High-Voltage Switchgear and Control Gear Standards) and IS 3427 (AC Metal Enclosed Switchgear and Control Gear for Rated Voltages above 1 kV and up to and including 52 kV).
The equipment offered shall be as per the standards specified in the bid specification and if the offered equipment is tested with any other international standards which is superior to the standards specified they can also be considered and the bidder has to submit the documentary evidence for the same.
3.9 | Design Details
The RMU shall be designed to operate at the rated voltage of 12 kV
It shall include, within the same metal enclosure, VCB and earthing switches. Suitable fool-proof interlocks shall be provided to the earthing switches to prevent inadvertent or accidental closing when the circuit is live.
The degree of protection required against prevailing environmental conditions, including splashing water and dust, shall be not less than IP 54 as per IS 12063.
The active parts of the switchgear shall be low maintenance type
The tank shall be made of minimum 2.5 mm thickness of stainless steel.
The Stainless Steel tank should be completely welded so as to ensure IP 67 degree of protection and shall be internal arc tested.
The RMU shall be suitable for mounting on its connecting cable trench.
For RMU enclosure, a suitably sized nameplate clearly identifying the enclosure and the electrical characteristics of the enclosed devices shall be provided.
The access to the cable compartment should be from the front of the switchgear only to have minimum operating & maintenance space at site
The RMU design shall be such that access to live parts shall not be possible without the use of tools.
The design shall incorporate features that prevent any accidental opening of the earth switch when it is in the closed position. Similarly, accidental closing of a VCB shall be prevented when the same is in an open position.
The RMU tank must be equipped with a suitable pressure relief device. The pressure relief must ensure that the escaping gases are dissipated to the rear bottom / top of the switchgear.
The complete RMU shall be tested in an accredited INDIAN laboratory and designed for an Internal Arc
3.1 | Earthing
There shall be continuity between metallic parts of the RMUs and cables so that there is no dangerous electric field in the surrounding air and the safety of personnel is ensured.
The RMU frames shall be connected to the main earth bars, and the cables shall be earthed by an Earthing Switch having the specified short circuit making capacity.
The Earthing Switch shall be operable only when the main switch is open. In this respect, a suitable mechanical fail-proof interlock shall be provided
The Earthing Switch shall be provided with a reliable earthing terminal for connection to an earthing conductor having a clamping screw suitable for the specified earth fault conditions. The connection point shall be marked with the earth symbol. The flexible connections between the earthing blade and the frame shall have a cross-section of at least 50 mm2 copper.
Supply and Providing Conventional type copper plate earthing with dual run copper strip should be provided as per standard requirement for 5 way RMU. (Tenderer should quote Inclusive of material cost of Copper Plate: 600 x 600 x 3mm, Copper Strip:50 x 3 mm ,GI pipes, charcoal ,salt, chemical compound, copper brazing required for copper plate and dual copper strip terminations.)
2 Numbers of conventional type copper plate earthing to be provided to 5 way RMU as per electricity norms. Earth resistance should be below 1 Ohm
The Earthing Switch shall be fitted with its own operating mechanism. In this respect, manual closing shall be driven by a fast acting mechanism independent of the operator's action
Copper Purity Certificate for 99.95 % should be submitted for the Copper Materials supplied to the consignee issued by Government Department ( MSME or Govt. authorized labs )
3.11 | Incomer
The Load Break Switches shall be maintenance free. With canopy doors open, the position of power contacts and earthing contacts shall be clearly visible from the front of the RMU through the Mimic facia.
The position indicator shall provide positive contact indication in accordance with IS 9920. In addition, the manufacturer shall prove the reliability of indication in accordance with IS 9921. These switches shall have three positions (or states), i.e., Open, Closed, and Earthed, and shall be constructed in such a way that natural interlocking prevents unauthorized operations
The switches shall be fully assembled, tested, and inspected in the factory.
Opening and closing shall be driven by a fast-acting mechanism independent of manual operator action
The switch and earthing switch mechanisms shall have a mechanical endurance of at least 1,000 operations
3.12 | Circuit Breakers
The Circuit Breakers shall be maintenance free and, when standing in front of the RMU with outdoor canopy doors open, their positions shall be clearly visible, through the Mimic facia. The position indicator shall provide positive contact indication in accordance with IS 9920. The breakers shall have three positions (or states), i.e., Open, Closed, and Earthed, and shall be constructed in such a way that natural interlocking prevents unauthorized operations. They shall be fully assembled, tested, and inspected in the factory
An operating mechanism shall be used to manually close the Circuit Breaker and charge the mechanism in a single movement. It shall be fitted with a local system for manual tripping. There shall be no automatic reclosing. The Circuit Breaker shall be capable of closing fully and latching against the rated making current. Mechanical indication of the OPEN, CLOSED, and EARTHED positions of the Circuit Breaker shall be provided.
Each Circuit Breaker shall operate in conjunction with a suitable protection relay under transformer feeder/ circuit phase and earth fault conditions. In addition, the Circuit Breaker shall be provided with a motorized operating mechanism that can be remotely controlled by the SCADA.
3.13 | Cable Termination
Bushings shall be conveniently located for working with the specified cables and shall allow for the termination of these cables in accordance with the prevailing practice and guidelines of cable manufacturers. The dimensions of the terminals shall be in accordance with IS 10601.
Cable Termination Cable entry shall be vermin proof, Maintenance free and Cable entry with proper supporting to firmly grip the cable to avoid any loose contacts and entry of moisture
The 11 kV XLPE cable size will be 3c x 120 Sq.mm (Aluminium)
Department will supply the required HT Cables.
Suitable standard make Cable termination Kits,bushing studs and cable clamps should be Supplied by the tenderer and execute the termination for RMU, HT SWITCH GEAR and 500KVA TRANSFORMER HT Side.
A non Ferro-magnetic cable clamp arrangement shall be provided for each cable to be terminated in the RMU.
A suitable arrangement for the Earthing Switches shall be provided so that these devices can be padlocked in the "Open" and "Closed" positions
A permanent "Live Cable" indication as per IEC 61958 shall be provided for each cable using a capacitor voltage divider
It shall be possible to test the core or sheath insulation of the cables without disconnecting the cables in the cable compartment, after accessing the cable compartment.
3.14 | Safety of Equipment
With respect to the RMU SF6-filled equipment, any accidental overpressure inside the sealed chamber shall be limited by the opening of a pressure-limiting device in the enclosure so that the gas will be released away from the operator and to the rear bottom or top of the tank without endangering the operator or anyone else in the vicinity of the RMU.
All manual operations, monitoring of open/close position of switches, live line indicators, FPI indication, SF6 gas pressure indication access to the cable compartment shall be carried out from the front of the RMU only.
3.15 | H T Metering facility including TOD Meter, CT/PT set to be provided - 1 set
3.15.1 | Current and Voltage Transformers. The RMU shall be provided with current and voltage transformers. These CTs & PTs shall meet the electrical and mechanical ratings as per the relevant standards.
Current Transformers 3 nos., ring type, single core CTs shall be provided in each incoming load break switch for metering purposes. A similar arrangement shall be provided in each circuit breaker cable compartment to mount a 3 nos., single-core, ring type CT for protection purposes.
The CTs shall conform to IS 2705. The design and construction shall be sufficiently robust to withstand thermal and dynamic stresses during short circuits. Secondary terminals of CTs shall be brought out suitably to a terminal block, which will be easily accessible for testing and terminal connections.
Further characteristics and features distinguishing CTs used for metering from CTs used for protection are listed as follows:
CTs for Metering: · Material: Epoxy resin cast/ Tape wound · Burden: 2.5VA · Ratio: 400-200-100/1 A · Accuracy Class: 0.5
CTs for Protection: · Material: Epoxy resin cast/ Tape wound · Burden: 2.5VA · Ratio: 400-200-100/1 A · Accuracy Class: 5 P 10
The RMU’s other CTs / sensors, i.e., those used by Fault Passage Indicators (FPIs), shall be supplied by the manufacturer. These CTs/sensors shall be an integral part of the FPI’s design to ensure that they properly match the requirements of the FPI
Voltage Transformers • A 3 phase single or 3 nos. single phase potential transformers shall be provided. These should be housed in a separate air insulated PT Panel, directly connected to the RMU through main bus. The burden per transformer shall not be more than 50 VA and the voltage ratio shall be 11000 V/ √ 3 /110 V/ √ 3. The accuracy class shall be 0.5.
• HRC fuses shall be provided on the HV side. The PTs shall be of cast epoxy-resin construction, and they shall conform to IS 3156. Their design and construction, in particular, shall be sufficiently robust to withstand the thermal and dynamic stresses during short circuits.
3.16 | Fault Passage Indicator for RMU The FPI shall be digital and facilitate quick detection of faulty section of line. The fault indication may be on the basis of monitoring fault current flow through the device. The FPI should be self-powered and should have internal lithium battery for external indication and setting of FPI in the absence of current. Each LBS shall be provided with 1No. FPI thus RMU shall be with 2 No. FPI
3.16.1 | The FPIs shall include: • Fault detection - Phase to phase and Phase to earth faults. • One potential-free output contacts for hardwiring to FRTUs. On this basis, the SCADA/DMS will be able to monitor phase / earth fault condition. • Local Fault Indications - FPI fault indication shall be LCD/LED. Every LBH shall be provided FPI with suitable CT ratio and the FPI shall support SCADA for remote reset and status of over current and earth fault. • Multiple reset option – • End of time delay (Adjustable from 2 to 16 Hrs) • Remote reset (Via potential free input contact of FPI) • Manual reset (Reset button on front panel of FPI) • Automatic reset on current restoration.
3.16.2 | The characteristics of the FPIs shall include: • Phase fault thresholds configurable from at least 100 to 800 A • Earth fault thresholds configurable from at least 20 to 200 A • Multiple number of steps for adjusting phase and earth fault thresholds. • Fault current duration range configurable from at least 40 ms to 100 ms in 20 ms steps and further 100 ms to 300 ms in 50 ms steps. • Variations with respect to these characteristics may be acceptable as long as they prove applicable and provide the same or better flexibility.
3.16.3 | Protection Relay
The RMU shall be equipped with self-powered numerical relays (Communicable relays shall be with auxiliary power which shall be given from battery but the tripping shall be self powered philosophy) communicable to trip the RMU circuit breaker
3.17 | General
The Circuit Breaker in the RMU shall be fitted with a communicable-type, self-powered numerical relay, i.e., one for each outgoing circuit breaker. The protection relay’s auxiliary contacts shall be provided for hardwiring to the FRTU. The relay shall also interface with the FRTU via an RS 232/485 port in order to send, as minimum, real-time readings using the MODBUS protocol.
The numerical relay shall be self-powered and should provide Inverse Definite Minimum Time (IDMT) and Instantaneous protection characteristics. On this basis, the relay as a minimum shall provide: • Phase Over current Protection (50/51) • Earth Fault Protection (50N/51N)
The relay shall be provided with an input for remote tripping, which shall be realized via an electric output pulse even without presence of phase current. A flag indicator shall be installed for signaling the occurrence of trip conditions
3.17.1 | Features and Characteristics
The numerical relay shall have the following minimal features and characteristics noting that variations may be acceptable as long as they provide similar or better functionality and/or flexibility
It shall be housed in a flush mounting case and powered by the RMU power supply unit.
It shall have three phase over current elements and one earth fault element
IDMT trip current settings shall be 50-200% in steps of 1% for phase over current and 10-80% in steps of 1% for earth fault.
Instantaneous trip current settings shall be 100-3000% in steps of 100% for phase over current and 100-1200% in steps of 100% for earth fault.
Selectable IDMT curves shall be provided to include, for example, Normal Inverse, Very Inverse, Extreme Inverse, Long Time Inverse, and Definite Time. Separate curve settings for phase over current and earth fault shall be supported.
For IDMT delay multiplication, the Time Multiplier Setting (TMS) shall be adjustable from 0.01 to 0.1 in 0.01 steps
The relay shall also be provided with: - Alphanumeric Liquid Crystal Display (LCD) for relay setting - Communications via a MODBUS RS232/RS485 port to provide the FRTU (and hence the DMS) with phase current measurements. It is also desirable that this same means of communication can be used by the FRTU to send setting and control commands to the relay. - Parameter change capability that is password protected.
3.17.2 | Power Supply and auxiliary power transformer
The RMU shall be fitted with a power supply, including batteries and battery charger, suitable for operating the motors of the On-load Isolators and Circuit Breakers. On this basis, the following operational specifications shall apply
The power supply unit shall conform to the following requirements - Input: 230 V AC nominal from the RMU’s auxiliary power transformer allowing for possible variations from 190 to 300 V AC - Output: Stable 24 V DC. - Batteries: 24 V DC (2 Nos of 12 V DC each)
The auxiliary power transformer shall be of suitable rating as per the load calculation and the Auxiliary power transformer shall be protected by HT fuses on primary sites and secondary with HRC fuses
The 24 V DC batteries shall have sufficient capacity to supply power to the following devices with a nominal backup of 4 hours: - RMU’s motors for a minimum of five (5) operations - RMU’s trip coils, close coils, FPI or any advanced technology with non storage type mechanism
The batteries shall be of sealed lead acid VRLA and shall have a minimum life of five (5) years at 25°C
The battery charger shall be fully temperature compensated
To prevent deep discharge of the batteries on loss of AC power source, the battery charger shall automatically disconnect all circuitry fed by the batteries following a user-adjustable time period or when the battery voltage falls below a preset value. If the battery voltage falls below the preset value, the time to fully recharge all batteries shall not exceed twenty-four (24) hours
An automatic battery checking device shall be provided to check the battery’s health and initiate a battery-failed alarm signal in case battery deterioration is detected. Such detection may be based on comparing measurement values with set values (e.g., internal resistance, voltage, etc.).
The battery charger shall be provided with an alarm displayed at the local control panel and remotely at the DAS to account for any of the following conditions: - Low battery voltage - Charger failed
3.17.3 | Multi-Function Transducer (MFT)
The RMU main incoming On-load switches circuits shall be equipped with Communicable Numeric relays (required for VCB only), and the multi-function transducers to be supplied by TGSPDCL, Hyderabad capable of providing distribution system voltage, current, power factor, power, and energy readings and is in the scope of the bidder. Provision for the wiring from metering current transformer shall be made available for connecting to MFT (MFT is not in the scope of the bidder shall be provided by the TGSPDCL, Hyderabad. The data from Communicable Numeric relay regarding the tripping functionalities shall be provided and data shall be integrated with the FRTU
3.18 | Construction The RMU shall be sufficiently sturdy to withstand handling during shipment, installation, and start-up without damage. The configuration for shipment shall adequately protect the RMU equipment from scraping, banging, or any other damage.
3.19 | Enclosures
All supplied enclosures shall be sized to provide convenient access to all enclosed components. It shall not be necessary to remove any component to gain access to another component for maintenance purposes or any other reason
The enclosures shall also be designed to ensure that the enclosure remains rigid and retains its structural integrity under all operating and service conditions with and without the enclosure door closed
The thickness of all side enclosure panels shall be at least 2 mm (minimum) and the thickness of bottom plate shall be at least 3 mm (minimum) of CRCA steel. The appropriate corrosion treatment and finish requirements shall apply to both inside and outside enclosure surfaces. Other required features are as follows
All enclosure panels shall be 7 tank Pre-treatment process & should be painted with UV Resistant Pure Polyester Powder coating. The powder coated sheet steel fabrication shall fulfill 700 Hrs of Salt spray test. The thickness of Painting/Powder coating shall be of 80-90 microns to withstand tropical heat and extremes of weather
Means, such as insulated heat shields and/or air vents, to prevent high temperatures from damaging the RMUs enclosed components. If air vents are installed, these vents shall in no way reduce the effectiveness of the enclosure’s protective characteristics.
A metal pocket attached to the inside of the front door to hold documentation, maintenance log sheets, and other such information.
Door opening mechanism with built-in key-lock facility suitable for padlocking. An opening mechanism that is less prone to breaking than a projecting door handle is preferred, e.g., a push-button opening mechanism
A grounding terminal including grounding bolt and lock washer for connecting a 50 mm2 copper or galvanized steel grounding conductor. The grounding bolt and lock washer shall be made of stainless steel.
Means of preventing moisture from condensing on electronic components mounted inside the enclosure proposed for housing the FRTU. If necessary, heaters providing adjustable thermostat-control within the range 20 to 60 ºC shall be installed in the enclosure for this purpose.
Means of enabling the SCADA to monitor the open/closed status of the enclosure door. A SCADA equipment alarm shall be produced whenever the enclosure door is open.
The outdoor RMU shall include having a minimum protection class of IP 54. It shall be tested in accordance with the latest IEC 60529 standard
The outdoor canopy shall have a hinged front access door with a two-point latch locking system with a latch operating lockable handle. The door shall be fitted with a perimeter flange and gasket (rubber or neoprene) to prevent the entrance of water. In addition, a means of monitoring and indicating that the door is open shall be provided.
Means of protection against rain water, and high levels of airborne dust, should be provided.
The door shall be fitted with a perimeter flange and gasket (rubber or neoprene) to prevent the entrance of water. In addition, a means of monitoring and indicating that the door is open shall be provided
3.2 | Motors
The RMU shall be fitted with spring charging 24V DC motors of high insulation class allowing the circuit breakers and load break switches to be operated without manual intervention.
In addition to allowing circuit breaker tripping by the RMU’s protection relays, the motorized operating mechanism shall be suitable for remote control by the SCADA. The motors along with the supplied control card and push buttons shall allow Utility’s personnel to electrically operate the circuit breakers and load break switches at site without any modification of the operating mechanism and without de-energizing the RMU.
3.21 | Front Plate · The front plate shall include a clear mimic diagram indicating RMU functionality. · The position indicators shall correctly depict the position of the main contacts and shall be clearly visible to the operator. The lever operating direction shall be clearly indicated.
3.22 | Inspection and Test Inspections and tests shall be performed to ensure RMU compliance with these Technical Specifications. Responsibility for conducting the inspections and tests shall rest with the Supplier. The Utility representatives will participate in the RMU inspections and will witness the testing as described in the following sub-clauses.
3.22.1 | Inspections
Utility’s representatives shall be allowed access to supplier’s facility where the RMU or its parts are being produced or tested. Such access will be used to verify by inspection that the RMU is being or has been fabricated and tested in accordance with the Technical Specifications.
The supplier shall give the utility’s representatives 15 days notice in writing concerning the date and place at which the equipment will be ready for inspection or testing. The supplier shall provide all the necessary assistance and facilities to utility’s representatives to carry such inspections and test witnessing.
The supplier shall provide any and all documentation that is necessary to complete the inspections. The representatives shall be allowed to inspect the supplier’s quality assurance standards, procedures, and records. Inspections, as a minimum, shall include checks on inventory, general appearance, cabling, drawing conformance, and labeling.
3.22.2 | Test Procedures
The supplier shall provide test plans and detailed procedures for all required testing. The plans and procedures shall ensure that each test is comprehensive and verifies proper performance of the RMU under test and, in this respect, shall be submitted for review and approval by the Utility.
The test plans shall include all routine tests and acceptance tests as per relevant BIS/IEC standards and shall describe the overall test process including the responsibilities of the test personnel and how the test results will be documented.
The test procedures shall describe the individual tests segments and the steps comprising each segment, particularly the methods and processes to be followed.
3.22.3 | Test Reports
The Tenderers should, along with the tender documents, submit copies of all Type test certificate of their make in full shape as confirming to IS 3427 / IEC 62271-100/200 of latest issue obtained from a International/National Govt. Lab/Recognized laboratory.
The above type test certificates should accompany the drawings for the materials duly signed by the institution that has type test certificate.
The supplier shall maintain complete records of all test results. The records shall be keyed to the test procedures.
Upon completion of each test, the supplier should submit a test report summarizing the tests performed and the results of the tests along with the complete details of type test reports inclusive of drawings
The bids received without complete type test reports along with drawings will be treated as non-responsive.
3.22.4 | Factory Acceptance Test
A formal factory acceptance test shall be conducted to ensure that the RMU has been designed to meet the utility’s functional requirements in all respects. Utility representatives shall witness the test on a representative RMU, and the test shall be carried out in accordance with the supplier’s test plan and procedures as approved by the Utility. Should the factory acceptance test prove unsatisfactory in any way, the Utility reserves the right to have further tests conducted and, if applicable, request further improvements in the supplier’s RMU design.
3.22.5 | Routine Factory Tests
These tests shall be carried out during RMU manufacture as a quality control measure, i.e., to ensure RMU to be delivered meets the Employer’s minimum requirements including all relevant standards. Recording and reporting the routine test results shall be the responsibility of the Supplier.
At the Utility’s discretion, Utility representatives will witness such testing. This may include requesting the Supplier to perform tests on RMU that the Supplier deems ready to be delivered to site. Should any such test prove unsatisfactory, the Utility reserves the right to have further tests conducted and for delivery not to take place until a mutually agreed course of action has been reached.
Further for additional reliability of the manufactured RMU it is mandatory to have the complete assembled tank tested for partial discharge
3.23 | Operating Manuals
The Supplier shall submit, operating manuals for all RMU components including items such as FPI, , and other equipment provided by the bidder. These manuals shall be in English. They shall include the RMU operating instructions. Context sensitivity shall be used to go directly to the appropriate place in the manual.
The manuals shall be organized for quick access to each detailed description of the operator procedures that are required to interact with the RMU functions. This shall include the procedures to define, build, edit, and expand all data points provided with the RMU.
The manuals shall present in a clear and concise manner all information that operators, including maintenance personnel, need to know to understand and operate RMU satisfactorily. The manuals shall make abundant use of diagrams and/or photographs to illustrate the various procedures involved.
3.23.1 | As-Built Documents and Drawings
The supplier shall submit as built documents including applicable drawings for review and approval. All deliverable documents and drawings shall be revised by the supplier to reflect the as- built RMU components including all the FPI & LLI. Any errors in or modifications to an RMU resulting from its factory and/or site acceptance test shall be incorporated. Within this same context, all previously submitted documents that are changed because of engineering changes, contract changes, errors, or omissions shall be resubmitted for review and approval. The successful bidder has to provide his quality document to Utility.
3.24 | Test certificates certified as per IEC 62271-100 / 200 or relevant IS Standard with latest amendments not more than 10 years. Following Test Certificates has to be submitted.
• Dielectric Withstand Test • Short time withstand - STC withstand test • Mechanical endurance test • Internal Arc test - IAC Test. • Tank & Cable compartment test (AFLR/AFL) for 1 sec as per IEC Standard IEC 62271-200. • Degree of protection test – IP test
Note: The bids received without complete type test reports along with drawings will be treated as non-responsive
3.25 | Warranty: Warranty Period: 5 Years from the date of commissioning. During the warranty period of 5 years in case of any flashover on bushings whether external or internal will lies in the scope of bidder.
3.26 | Patent Rights The Supplier will indemnify the Purchaser against all third-party claims of infringement of patent, trademark, or industrial design rights arising from use of the Materials/ equipment or any part thereof.
3.27 | Special conditions
Bear all the charges for submission of RMU drawings to Electricity dept.
Vendor must coordinate with TGSPDCL, Hyderabad (TELANGANA STATE POWER DISTRUBUTION CORPORATION LTD). for approval of 5Way RMU (Scada Compatible Monitoring & Controlling) installation, revenue metering arrangements, CT/PT ratios, and relay settings, inspection etc
Any deviations from this specification must be clearly listed in the bid.
Bidders must submit short-circuit and ampacity calculations to confirm adequacy of cable sizing (120 mm²).
Payment Terms:
80% of the cost of materials/service/insurance/ Transportation and 100% GST charges in item No.1, 3, 7, 8, 9, 10, 13 & 17 under Annexure- A will be released upon supply of 5way RMU panel and the said items in good condition at site. The 100% payment in respect of remaining items and work balance 20% will be released after satisfactory completion of DSITC of 5way RMU at Doordarshan Geo Diversity Disaster Recovery Centre, Chintalakunta, LB Nagar, Hyderabad
SECTION – II SCHEDULE OF REQUIREMENTS
DD requires the following equipment/ services as per technical specifications detailed under section-I. The present requirement is for Doordarshan Geo Diversity Disaster Recovery Centre (GDDRC) at Chintalakunta, LB Nagar, Hyderabad
The tenderer shall quote prices of each item separately in price bid with necessary break up details keeping in view the following
i. Make and model of each item, to be indicated. ii. Indenter reserves the right to choose & decide the quantity of equipment at the time of finalization of tender.
S.No | DESCRIPTION | QTY. | Make & Model | Tenderer's offer / Compliance (Numerical value to be given)
1 | Supply of 11kV 3 phase, 630Amps, Motorized SCADA compatible ( Monitoring & Controling ) , SF6 Insulated Outdoor, 5Way Ring Main Unit (RMU) consists of: | 1 set
(a) | SF6 Load Break Switch (LBS) | 2 Nos
(b) | Vacuum Circuit Breakers 630A (CB) | 3 Nos
(c ) | Potential Transformers | 1 Set
(d ) | Current Transformers | 1 Set
(e ) | Bus Bars | 1 Set
(f ) | Digital multifunction Meters | 1 Set
(g ) | Over current Relay | 1 Set
(h ) | Earth Fault Relay | 1 Set
(i ) | HT Metering Facility including TOD Meter | 1 Set
(j ) | Cable Termination as required | 1 Set
(k ) | Cable Glands as required | 1 Set
(l) | Trickle Charger with Sealed maintenance free battery (of reputed make). | 1 Set
2 | Insurance, Transportation and unloading at site of the above switchgear | 1 Job
3(a) | Installation, including Civil foundation, consumable hardware, inter connecting control cabling with cables, input & output supply cable connections with kits to and fro from HT panel and extension of earth from clients earth bus etc. | 1 Job
(b) | Testing & Commissioning, of the above HT Switchgear. | 1 Job
(c ) | Complete Installation material for the above switch gear. | 1 Job
The tenderer may visit the site before submitting the tender, to assess the quantum of work to avoid any delay while execution
4 | Special tools if any required for field maintenance and repair of VCBs (List of Tools to be enclosed). | 1 Set
5 | Book of Instructions for Installation, operations Testing, Commissioning and maintenance including finalized drawings. | 4 Sets
Note : Required Length of HT Cables 120 Sqmm ,XLPE ,3 CORE ,Armoured Cables will be Supplied by the Department
SECTION -III
Schedule-A
GUARANTEED TECHNICAL PARTICULARS FOR OUTDOOR 5WAY RMU
PART 1
1 | Manufacturer’s Name and Country of origin
2 | Manufacturer’s Design/Type/Model
3 | Material used for making the body of the RMU
4 | Standards of manufacturing
5 | Whether painting for RMU is done as per standards
6 | Whether the enclosure is anti-corrosive
7 | Whether RMU metal clad has sufficient space for integration of: • Vacuum Circuit breaker • Sufficient space for inspection, testing, etc. • Earthing arrangements • Terminal output points for automation • Sufficient arrangement for future extension with Circuit Breakers
8 | Maximum withstanding ambient temperatures
9 | Spacing between live parts to earth
10 | Whether RMU are designed to withstand all weather conditions including chemical industry and polluted areas
11 | Period of guarantee of the RMU
12 | Over all dimensions of the 5 Way RMU (L x W x H).
13 | Material & Gauge of material used for fabrication of the RMU
14 | Whether RMU is manufactured as per IEC/IS standards to hold SF6 gas without leakage
15 | Whether RMU has provision for sensors for temperature compensated pressure measurement in the relevant gas compartment to monitor the pressure of SF6 gas
16 | Whether RMU is sealed pressure system
17 | Weight of RMU complete with operating mechanism
18 | RMU is provided with necessary take off terminals for automation
19 | Whether gas chamber is made of stainless steel
SCHEDULE OF GUARANTEED PARTICULARS FOR BREAKER
PART 2
1 | Manufacturer’s Name and Country of origin
2 | Manufacturer’s Design / Type ref/ Model.
3 | Material used for making the body of the breaker
4 | Standards of manufacturing
5 | Whether the breaker is manufactured as per IEC/IS standards Please give Standards no.
6 | Maximum temperature withstand of the breakers
7 | 1 Spacing between live part to Earth inside the breaker 2 Spacing between poles
8 | Period of guarantee of the breaker
9 | Rated frequency
10 | Rated voltage
11 | Highest system voltage
12 | Rated current
13 | Short time current rating with duration
14 | Certificate or report of short circuit type test
15 | Rated operating duty cycle
16 | Short circuit breaking current (a) Symmetrical (b) Symmetrical at rated voltage (c) Asymmetrical at rated voltage (i) Per Phase (ii) Average (d) DC Component
17 | Arcing time (At rated breaking current) in ms
18 | Opening time
19 | Total break time in mili sec. (a) At 10% rated interrupting capacity (b) At rated interrupting capacity
20 | Breaking Current (a) Rated out of phase current (b) Rated cable charging current (c) Rated fault level MVA (d) Rated capacitor breaking current
21 | Make time in ms
22 | Maximum temperature rise over ambient
Main contacts Terminals
23 | Rated restriping voltage at 100% and 50% rated capacity. a) Amplitude factor b) Phase factor c) Natural frequency d) R.R.R.V. (Volts/micro sec.)
24 | Dry 1 minute power frequency withstand test voltage a) Between line terminal and earth KV RMS b) Between terminals with breaker contacts open KV RMS.
25 | 1.2/50 full wave impulse withstand test voltage a) Between line terminal and earth KVp. b) Between terminals with breaker contacts open KVp.
26 | VCB interrupter make
27 | Contact separation distance
28 | Type of main contacts
29 | Contact pressure
30 | Contact resistance
31 | Life of the interrupter (in number of operations) (i)Tripping at rated current (ii)Tripping at maximum fault current.(Allowable maximum erosion 3 mm) (iii)Mechanical operations
32 | Details of main contacts making contact with the breaker truck with the panel
33 | Control circuit voltage AC/DC
34 | Whether trip free or not
35 | Whether all the interlocks provided
SCHEDULE OF GUARANTEED PARTICULARS FOR EARTHING SWITCHERS
PART 3
SI.No | Description | Load Break Switch | Isolator (Earthing Switch)
1 | Manufacturer’s Name and Country of origin
2 | Manufacturer’s Design / Type ref/ Model
3 | Material used for making the body of the isolators
4 | Standards of manufacturing
5 | Whether the isolators & earth positions are manufactured as per IEC/IS standards
6 | Maximum temperature withstand of the isolators & earth switches
7 | 1) Spacing between live part to Earth 2) Spacing between fixed and moving contacts in the open position
8 | Period of guarantee of the Earthing switches
9 | Rated frequency
10 | Rated voltage
11 | Highest system voltage
12 | Rated current
13 | Short time current rating with duration
14 | Certificate or report of short circuit type test
15 | Rated operating duty cycle
16 | Short circuit breaking current
17 | Arcing time (At rated breaking current) in ms.
18 | Opening time
19 | Whether all the interlocks provided
SCHEDULE OF GUARANTEED TECHNICAL PARTICULARS FOR SELF POWERED MICRO- PROCESSOR BASED NUMERICAL RELAYS
PART 4
1 | Manufacturer’s Name and Country of origin
2 | Manufacturer’s design / Ref. Type
3 | Applicable Standards
4 | Current Setting range for (a) Over current relay (b) Earth fault Element | IDMT Definite Time
5 | Whether the relay has the in-built facilities of IDMT, OL, EL
6 | Details of IDMT Characteristics
7 | Accuracy for different settings and limits of errors
8 | Whether Alpha numeric / LED display
9 | Whether compatible for 1 A CT Secondary
10 | Whether draw out type
11 | Type of case
12 | Reset time
13 | Burden of relay
14 | Maximum and Minimum, operating ambient air temp
15 | Whether technical literature pamphlets about the relay offered
16 | Period of guarantee.
17 | Certificate of Proof for Electro Magnetic Interference
18 | Communications port – RS 232 / RS 485
19 | Communication Protocol – MODBUS
Bill of Materials ( Without Price)
S.No. | Description | Qty | Unit | Tenderers’ Compliance
1 | Supply of 11kV 3 phase, 630Amps, Motorized SCADA compatible ( Monitoring & Controlling ), SF6 Insulated Outdoor, totally enclosed, 5Way Ring Main Unit (RMU) Consisting of Incoming LBS - 2 Nos and Outgoing CB - 3 Nos. with voltage and current Metering on all incoming/Outgoing feeders including all the protective devices confirming to standard :IS3427/1997 amended to date as detailed below and conforming to TGSPDCTL ,Hyderabad requirements. RMU design and CT/ PT ratio should be suitable for 320kVA Maximum Demand. | 1 | Set
2 | Insurance, transportation and unloading of RMU at site | 1 | Job
3 | Design, fabrication and construction of RCC foundation / plinth for 5Way RMU panels including anchor bolts, cable trench interface panel to panel and civil works as recommended by OEM and as per TGSPDCL Hyderabad norms. | 1 | Job
4 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 11kV Feeder structure to Outdoor type RMU incomer panel. Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCL ,Hyderabad norms. Payment shall be as per actuals | 20 Mtr (Approx) | Rate/ Meter
5 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from Outdoor type RMU to 4 Panel HT Switchgear Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCL ,Hyderabad norms. Payment shall be as per actuals | 40 Mtr (Approx) | Rate/ Meter
6 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 4 Panel HT Switchgear to 500 kVA Transformers – 2 Nos. Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCLTL ,Hyderabad norms. Payment shall be as per actuals. | 20 Mtr (Approx) | Job Rate/ Meter
7 | Supply and fixing of outdoor heat shrinkable / end standard make termination kits for 11 kV, 120Sq mm XLPE HT Cable for RMU | 10 | Nos
8 | Supply and fixing of indoor heat shrinkable / end standard make Cable termination kits for 11 kV, 120Sq mm XLPE HT Cable for HT Switchgear Panel and 500KVA Indoor Transformers – 2 Nos | 8 | Nos
9 | Supply and fixing of indoor heat shrinkable / end standard make Cable termination kits for 11 kV, 120Sq mm XLPE HT Cable 500KVA Indoor Transformers – 2 Nos | 2 | Nos
10 | Supply and Providing conventional type Copper plate earthing system for RMU including termination, interconnections, test links and all accessories as per the drawing enclosed in Annexure – C (Diagram -2) for completion of the earthing.Copper Strips 50 x 3 mm (As per Actuals), Copper Plate, GI Pipe,and any other required materials to complete the Earthing system should be supplied by the tenderer. Copper Purity Certificate for 99.95% to be submitted for the copper materials supplied for Earthing system. | 2 | Set Rate/ one Earth
11 | Excavation and Laying Copper strip from Earth pit terminal to the 5way RMU and terminations as per TGSPDCL, Hyderabad Norms . Payment shall be as per actuals at the Site | 20 Mts (Approx) | Rate Per Meter
12 | Testing of High Voltage HT Cables including insulation resistance, continuity and sheath integrity before laying of cable | 1 | Job
13 | Provision for cable glands in RMU, and providing cable glands, lugs, ferrules, cable clamps and other termination accessories for HT cables. | 1 | Lumpsum
14 | System integration, trial run, and commissioning of complete 11kV power supply system including synchronization with existing network | 1 | Job
15 | Preparation and submission of as-built drawings, test certificates, O & M Manuals and commissioning reports and Towards charges for submission of RMU drawings to TGSPDCL, Hyderabad | 1 | Job
16 | Erection/Installation, testing and commissioning of 5 Way RMU units including obtaining approval from, TGSPDCL ,Hyderabad / Central Electricity Authorities. | 1 | Job
17 | Tripping battery system complete with trickle charger operating from 230V mains for use with the tripping circuit of above switch board ( if necessary) | 1 | Set
18 | Any other material/work necessary to complete the SITC and Approval from CEA and any other Department |  | Lumpsum
Consignee : The Deputy Director General (Engg.),Doordarshan Kendra, Ramanthapur,Hyderabad - 500 013. Mobile: 9958787549
Additional Information to be provided along with Technical bid
1 | Due Date of the Tender
2 | Validity of the quotation ( 120 days)
3 | Delivery Period ( 1 Month)
4 | Warranty (5 Years)
5 | SGST/CGST/IGST/Registration No
6 | HSN / SAC Code
7 | Company Registration No
8 | PAN No
9 | Any other information
10 | Undertaking