## Sheet1
Item Number | Item Title | Item Description | Item Quantity | Unit of Measure | Consignee ID | Delivery Period (In number of days)
1 | Supply of 11kV 3 phase, 630Amps, Motorized SCADA compatible Monitoring and Controlling , SF6 Insulated Outdoor, totally enclosed, 5Way Ring Main Unit RMU | Supply of 11kV 3 phase, 630Amps, Motorized SCADA compatible Monitoring and Controlling , SF6 Insulated Outdoor, totally enclosed, 5Way Ring Main Unit RMU Consisting of Incoming LBS 2 Nos and Outgoing CB 3 Nos. with voltage and current Metering on all incoming or Outgoing feeders including all the protective devices confirming to standard IS3427 1997 amended to date as detailed below and conforming to TGSPDCTL ,Hyderabad requirements. RMU design and CT PT ratio should be suitable for 320kVA Maximum Demand. | 1 | Set | DDE_DDKHYD | 30
2 | Insurance, transportation and unloading of RMU at site | Insurance, transportation and unloading of RMU at site | 1 | Job | DDE_DDKHYD | 30
3 | Design, fabrication and construction of RCC foundation or plinth for 5Way RMU panels | Design, fabrication and construction of RCC foundation / plinth for 5Way RMU panels including anchor bolts, cable trench interface panel to panel and civil works as recommended by OEM and as per TGSPDCL Hyderabad norms. | 1 | Job | DDE_DDKHYD | 30
4 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 11kV Feeder structure to RMU panel | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 11kV Feeder structure to Outdoor type RMU incomer panel. Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCL ,Hyderabad norms. Payment shall be as per actuals | 20 | Mtr | DDE_DDKHYD | 30
5 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from Outdoor type RMU to 4 panel HT Switchgear | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from Outdoor type RMU to 4 Panel HT Switchgear Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCL ,Hyderabad norms. Payment shall be as per actuals | 40 | Mtr | DDE_DDKHYD | 30
6 | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 4 panel HT Switchgear to 500 kVA Transformers 2 Nos. | Laying of 11kV, 3 core, 120 Sqmm XLPE, Aluminium Armoured HT cable from 4 Panel HT Switchgear to 500 kVA Transformers 2 Nos. Work includes excavation of cable trench, laying of HT Cable, filling with sand cushioning, bricks and closing with protective covers trench, providing cable markers and back filling as per TGSPDCLTL ,Hyderabad norms. Payment shall be as per actuals. | 20 | Mtr | DDE_DDKHYD | 30
7 | Supply and fixing of outdoor heat shrinkable end standard make termination kits for 11 kV, 120Sq mm XLPE HT Cable for RMU | Supply and fixing of outdoor heat shrinkable / end standard make termination kits for 11 kV, 120Sq mm XLPE HT Cable for RMU | 10 | Nos | DDE_DDKHYD | 30
8 | Supply and fixing of indoor heat shrinkable or end standard make Cable termination kits for 11 kV, 120Sq mm XLPE HT Cable for HT Switchgear Panel and 500KVA Indoor Transformers 2 Nos. | Supply and fixing of indoor heat shrinkable or end standard make Cable termination kits for 11 kV, 120Sq mm XLPE HT Cable for HT Switchgear Panel and 500KVA Indoor Transformers 2 Nos | 8 | Nos | DDE_DDKHYD | 30
9 | Supply and fixing of indoor heat shrinkable or end standard make Cable termination kits for 11 kV 120Sq mm XLPE HT Cable 500KVA Indoor Transformers 2 Nos | Supply and fixing of indoor heat shrinkable or end standard make Cable termination kits for 11 kV 120Sq mm XLPE HT Cable 500KVA Indoor Transformers 2 Nos | 2 | Nos | DDE_DDKHYD | 30
10 | Supply and Providing conventional type Copper plate earthing system for RMU | Supply and Providing conventional type Copper plate earthing system for RMU including termination, interconnections, test links and all accessories as per the drawing enclosed in Annexure C Diagram 2 for completion of the earthing.Copper Strips 50 x 3 mm As per Actuals, Copper Plate, GI Pipe,and any other required materials to complete the Earthing system should be supplied by the tenderer. Copper Purity Certificate for 99.95 Percentage to be submitted for the copper materials supplied for Earthing system. | 2 | Sets | DDE_DDKHYD | 30
11 | Excavation and Laying Copper strip from Earth pit terminal to the 5way RMU and Terminations as per TGSPDCL Hyderabad norms | Excavation and Laying Copper strip from Earth pit terminal to the 5way RMU and terminations as per TGSPDCL, Hyderabad Norms . Payment shall be as per actuals at the Site | 20 | Mtr | DDE_DDKHYD | 30
12 | Testing of High Voltage HT Cables | Testing of High Voltage HT Cables including insulation resistance, continuity and sheath integrity before laying of cable | 1 | Job | DDE_DDKHYD | 30
13 | Provision for cable glands in RMU, and providing cable glands, lugs, ferrules, cable clamps and other termination accessories for HT cables. | Provision for cable glands in RMU, and providing cable glands, lugs, ferrules, cable clamps and other termination accessories for HT cables. | 1 | Lumpsum | DDE_DDKHYD | 30
14 | System integration, trial run, and commissioning of complete 11kV power supply system including synchronization with existing network | System integration, trial run, and commissioning of complete 11kV power supply system including synchronization with existing network | 1 | Job | DDE_DDKHYD | 30
15 | Preparation and submission of as-built drawings, test certificates, O and M Manuals and commissioning reports and Towards charges for submission of RMU drawings to TGSPDCL, Hyderabad | Preparation and submission of as-built drawings, test certificates, O and M Manuals and commissioning reports and Towards charges for submission of RMU drawings to TGSPDCL, Hyderabad | 1 | Job | DDE_DDKHYD | 30
16 | Erection or Installation, testing and commissioning of 5 Way RMU units including obtaining approval from, TGSPDCL ,Hyderabad Central Electricity Authorities. | Erection/Installation, testing and commissioning of 5 Way RMU units including obtaining approval from, TGSPDCL ,Hyderabad / Central Electricity Authorities. | 1 | Job | DDE_DDKHYD | 30
17 | Tripping battery system complete with trickle charger operating from 230V mains for use with the tripping circuit of above switch board if necessary | Tripping battery system complete with trickle charger operating from 230V mains for use with the tripping circuit of above switch board ( if necessary) | 1 | Set | DDE_DDKHYD | 30
18 | Any other material or work necessary to complete the SITC and Approval from CEA and any other Department | Any other material/work necessary to complete the SITC and Approval from CEA and any other Department | 1 | Lumpsum | DDE_DDKHYD | 30