## Technical Bid
प्रसारभारती / PRASAR BHARATI (भारतकालोकसेवाप्रसारक/ INDIA’S PUBLIC SERVICE BROADCASTER) अपरमहानिदेशककाकार्यालय(अभि.) (द.क्षे..) / O/o. ADDL. DIRECTOR GENERAL (E)(SZ) आकाशवाणीएवंदूरदर्शन / AKASHVANI& DOORDARSHAN स्वामीशिवानंदासालै, चेन्नई/ SWAMY SIVANANDA SALAI, CHENNAI – 600 005. e-mail:adgszpurchase@prasarbharati.gov.in
TECHNICAL BID
Tender No |  | J-11014/5/2026-PURCHASE-ADG(E)-(SZ) Dated: 31-07-2026
Description of work |  | Supply of HT/LT Power Supply Cables for Geo Diversity Disaster Recovery Centre,Chintalakunta, LB Nagar, Hyderabad
Name of the Company
Quotation No & Date
Complete Postal Address
E-Mail
Phone/cell
Make & Model of The Offered Product
Specification for Supply of HT/LT Power Supply Cables for DOORDARSHAN,GDDRC Project, Hyderabad.
120 SQ.MM, 11kV, 3 CORE, XLPE ARMOURD ALUMINIUM HT CABLE:
Sl No | Technical Parameter | DD’s Requirement |  | Tenderer's compliance
1 | Size (Cross Sectional Area) | 120 Sq.mm
2 | Insulation Type | XLPE
3 | Insulation Thickness | 5.50 mm (approx.)
4 | Armour Type | Flat Strip
5 | Minimum Inner Sheath Thickness | 0.70 mm (approx.)
6 | Nominal Armour Strip Dimension | 4 x 0.80 mm
7 | Minimum Outer Sheath Thickness | 2.52 mm (approx.)
8 | Overall Diameter of Cable | 65 mm (approx.)
9 | Conductor Resistance | 0.325 Ohm / Km (approx.)
10 | Reactance of Cable at 50 Hz | 0.112 Ohm/ Km (approx.)
11 | Capacitance of Cable | 0.23 μF/ Km (approx.)
12 | Current Rating (Ground/Duct/Air) | 220/190/260 Amps
13 | Short Circuit Current for 1sec Duration | 12kA
14 | Conductor Screening | Extruded Semiconductor compound
15 | Conductor | Stranded compacted circular Aluminium as per Class II of IS:8130
16 | Insulation Screening | Extruded semiconducting compound followed by Helically wrapped copper tape
17 | Filler | PVC filler
18 | Inner Sheath | Extruded PVC type ST-2 as per IS:5831
19 | PVC Type | ST-2/FR/FRLS Type
20 | Outer Sheath | Extruded PVC type ST- 2 as per IS:5831
21 | PVC Type | ST-2/FR/FRLS Type
240 SQ.MM 4 CORE, 415V, XLPE ARMOURD ALUMINIUM LT CABLE:
1 | Size (Cross Sectional Area) | 240 Sq.mm
2 | Insulation Type | XLPE
3 | Insulation Thickness | 1.70 mm (approx.)
4 | Armour Type | Flat Strip
5 | Minimum Inner Sheath Thickness | 0.60 mm (approx.)
6 | Nominal Armour Strip Dimension | 4 x 0.80 mm (approx.)
7 | Minimum Outer Sheath Thickness | 2.20 mm (approx.)
8 | Overall Diameter of Cable | 54 mm (approx.)
9 | Conductor Resistance at 90˚ C | 0.162 Ohm / Km (approx.)
10 | Reactance of Cable at 50 Hz | 0.072 Ohm / Km (approx.)
11 | Capacitance of Cable | 0.31 μF/ Km (approx.)
12 | Current Rating (Ground/Duct/Air) | 327/276/392 Amps
13 | Short Circuit Current for 1sec Duration | 23kA (Approx.)
14 | Conductor Screening | Extruded Semiconductor compound
15 | Conductor | Stranded compacted circular Aluminium as per Class II of IS:8130
16 | Inner Sheath | Extruded PVC type ST-2 as per IS:5831
17 | PVC Type | ST-2/FR/FRLS Type
18 | Outer Sheath | Extruded PVC type ST-2 as per IS:5831
19 | PVC Type | ST-2/FR/FRLS Type
Bill of Materials ( Without Price)
S.No. | Description |  | Qty | Make of the Cable
1 | 120sqmm, 11KV, 3C Armoured HT XLPE Aluminium Cable |  | 270 Meter
2 | 240 Sqmm, 415V, 4C Armoured LT XLPE Aluminium Cable |  | 500 Meter
Consignee: The Assistant Engineer/Installation officer ( Shri.Banoth Kishore Kumar, AE), LB Nagar, Chintalakunta, Hyderabad
Information to be provided along with Technical bid
1 | Due Date of the Tender
2 | Validity of the quotation(120 days)
3 | Delivery Period (45 days )
4 | Guarantee/Warranty ( One Year)
5 | GST Registration No
6 | PAN No
7 | Any other information