## Financial Bid
AKASHVANI, PRASAR BHARATI
Schedule of Bid
NIT No: 05/NIT/SEE/CCW/NGP/2026-27
Name Of Work :- AARMO Electricals works at NFAI-NFDC at PUNE for 2026-27.(Sub Head:- Comprehensive Maintenance of Electrical Installation, Operation of water supply pump sets at NFAI Ph- I & II and Staff quarters.)
NAME OF THE CONTRACTOR/FIRM
S. No | Description of Item | Quantity | Unit | Rate | Amount
NFAI Ph-I (Law College Road) & Staff Quarters (Ganeshkhind Road)
1 | Carrying out Day to day Annual comprehensive maintenance of internal electrical installations approximate Built Up Area of 6165.95 Sq. Mtrs (out of which 4524.19 Sq.Mrs Non residential aera at NFDC-NFAI HQ and 1623.76 Sq.Mtr. of residential area located at AIR Staff Quarter premises) with sufficient manpower as required including including collection of water from PMC in sump Tank and operation of water supply pump sets as per requirement, and attending the rescue of trapped passengers in the Lifts installed in the buildings and to operate the lifts during VIP visits, noting down the complaints, and attending to them by replacement of accessories like switches, sockets, ceiling fan condenser, fan regulator, capacitors, ballast, LED Drivers, holders, miniature circuit breakers, MCCB, isolators, residual current circuit breakers, industrial sockets, MCB distribution boards, thermostat /coils in geyser units, repairs to ceiling fans by rewinding, replacement of bearings, shaft etc. including all types of fittings, DB's, LT panel boards, feeder pillars, street lights, compound lights, gate lights, pumps and associated wiring and cables inside the campus including supply and replacement of fuses (HRC & Rewirable), bolts, nuts, cable end terminations, damaged PVC sleeves, testing etc. in total all electrical installations, taking acknowledgement from the occupant assisting the Department in updating data etc.,as required. | 12 | Month | 83801 | 1005612
NFAI Ph-II (Kothrud)
2 | Carrying out Day to day Annual comprehensive maintenance of internal electrical installations approximate Built Up Area of 5867.55 Sq. Mtrs ( Office Block- 1450.43, Auditorium -327.17, Sevice Block-986.04, Vualt Block-2537.64, Temporary Shed-351.0 and Nitrate Film Vaults-215.27 SqMtrs) with sufficient manpower as required including collection of water from PMC in sump Tank and operation of water supply pump sets as per requirement, and attending the rescue of trapped passengers in the Lifts installed in the buildings and to operate the lifts during VIP visits, noting down the complaints, attending to them by replacement of accessories like switches, sockets, ceiling fan condenser, fan regulator, capacitors, ballast, LED Drivers, holders, miniature circuit breakers, MCCB, isolators, residual current circuit breakers, industrial sockets, MCB distribution boards, thermostat /coils in geyser units, repairs to ceiling fans by rewinding, replacement of bearings, shaft etc. including all types of fittings, DB's, panel boards, feeder pillars, street lights, compound lights, gate lights, pumps and associated wiring and cables inside the campus including supply and replacement of fuses (HRC & Rewirable), bolts, nuts, cable end terminations, damaged PVC sleeves, testing etc. in total all electrical installations, taking acknowledgement from the occupant assisting the Department in updating data etc.,as required. | 12 | Month | 86237 | 1034844
Maintenance of Sub Station Equipment's
Routine & Preventive Maintenance at Phase - I
3 | Overhauling & Servicing of HT 11 KV VCB as per the maintenance schedule as mentioned below and as per the manufacturer's recommendations, cleaning all indoor portion checking all accessories, replacing of minor defective parts, including disconnecting, dismantling Refitting in the panel restoring the supply in safe manner etc. as required. | 3 | Each | 50301 | 150903
a | Overhauling of 11 KV panel mainly comprising of breaker module, closing, tripping and spring charging test.
b | Testing of Over current & Earth Fault relays for each feeder.
c | Testing of Trafo; Aux. relays for each feeder.
d | Testing of Current transformer (CT) by Primary and Secondary Injection method.
e | Testing of Potential transformer (PT) by Primary and Secondary Injection method.
f | Testing of control circuits.
g | Checking of Tripping circuit/ system; correcting the same.
(Note: Servicing warranty to be provided for a period of 1 (One) year.)
4 | Calibration of Microprocessor based relays in 11 KV, VCB panel including auxiliary relay, earth fault relay, over current relay, testing and cleaning etc. as required. | 3 | Each | 8170 | 24510
(Note: Calibration warranty to be provided for a period of 1 (One) year.)
Routine & Preventive Maintenance at Phase - II
5 | Overhauling and servicing of HT 22 KV 4 pole structure comprising of GOD, lightening arrestor, fuses etc restoring the supply in safe manner etc as required. | 1 | Job | 6401 | 6401
6 | Painting of HT 22 KV 4 pole structure alongwith Aluminium paint and redoxide primer by scrapping the structure etc restoring the supply in safe manner etc as required. | 1 | Job | 15235 | 15235
7 | Overhauling & Servicing of air circuit breaker up to 800 amps, 440 volts, 3 phase including testing with following scope of works etc. as required. | 8 | Each | 8170 | 65360
Phase I = 5 Nos, Phase II = 3 Nos
a | (I) Dismantling the breaker except the MSW mechanism
(II) Cleaning of component with petrol & contacts with CRC, removing old greaser & dust from racking roller & earth knife
(III) Changing the damaged / rusted parts
(IV) Re-assembling the breaker
(V) Tightening the fasteners of the mechanism & back panel
b | Check condition of arcing contact and gap between fixed and moving arcing contacts, Checking the reset mechanism, tripping of breaker through push button, Checking tripping of ACB through protection release, Tripping of ACB manually through volt metric release. Checking and adjust freeness of release trip rods, Checking presence and proper tightening of hardware. Checking presence of all cir-clips ,Checking condition of ACB wiring and replacing if required Checking proper closing of all poles together, Checking alignment of SIC and it’s operation Checking scraping earth alignment Checking condition of arc chute, Checking and alignment of U/V release, Checking ACB tripping through shunt release, Checking of spring charging operation., Checking of resetting operation.
c | Setting:
(I) Set contact gaps
(II) Set pull rod
(III) Set trip rod
d | (I) Lubricating the inner mechanism rollers & other linkages
(II) Applying grease for solid racks , racking roller & earth knife
(III) Apply petroleum jelly on cluster contacts
8 | Filtration of transformer oil up to satisfactory dehydration, acidity test & high voltage test of following transformers including servicing, checking & tighten of HT & LT connections, Meggering the HT & LT (Primary & secondary) cables, insulation test of transformer Overall testing of all protection systems complete etc. as required.
8.1 | 500 KVA ( Oil - 400 + 400 Ltrs) Phase - I | 800 | Ltr | 35 | 28000
8.2 | 315 KVA ( Oil - 550 + 475 Ltrs) Phase - II | 1025 | Ltr | 35 | 35875
9 | Toping of new transformer oil to all 4 nos transformer up to satisfactory level etc. | 300 | Ltr | 164 | 49200
10 | Rectifying of leakage of oil from core body at terminal block of transformer by replacement of necessary size gasket packing's, welding at conservator , checking of Buchholz relay further testing & rectification of all miner leakages complete etc. as required. | 4 | Job | 17953 | 71812
11 | Supplying & fixing of Silica gel container along with silica gel for breather of transformers. | 4 | Each | 1028 | 4112
|  |  |  | Total | 2491864
NAME OF THE CONTRACTOR/FIRM
S.No | Name of Component | Estimated cost (in Rs) | Above or Below or at Par | % In Figures | Total Cost
1 | 2 | 4 | 5 | 6 | 7
1 | ARMO Electricals works at NFAI-NFDC at PUNE for 2026-27.(Sub Head:- Comprehensive Maintenance of Electrical Installation, Operation of water supply pump sets at NFAI Ph- I & II and Staff quarters.) | 2491864 |  |  | 0
| Total Amount |  |  |  | 0
Note:
Annual Comprehensive Maintenance for subsequent years shall be carried out 100 % Hundred Percent) of Items of Schedule of work for the NIT and annual enhancement in AMC rates shall be 6 % (Six Percent) of that rate on chargeable basis for the balance period i.e.: 2nd Year 100% of (X) x 1.06 3rd Year 100% of (X) x (1.06)², as per Schedule of work and terms & conditions through separate agreement on chargeable basis
Executive Engineer (Elect)